## Cooling-Calc-New
Cooling Tower Water Balance and Calculation (20260410~)
입력 필요 시 조정 자동산출 고정
냉각 용량 | 1000 | RT | 항목 | 보충수 | 순환수 | Cycled | Limit | 현재 농축배수 |  | 1.55
집수조 | 0 | m3 | 전도도 | 435 | 537 | 2610 |  | 현재 블로우량 |  | 4.4594 | m3/Hr | =(LOG(G5)-1)/10 | 0.173
보유수량 | 37.85 | m3 | 총경도 | 34 | 46 | 204 |  | 목표 농축배수 |  | 6 |  | =LOG(G6)-0.4 | 1.2628
순환수량 | 681.3 | m3/Hr | 전알칼리 | 70 | 80 | 420 |  | 목표 블로우량 |  | 0.49054 | m3/Hr | =LOG(G7) | 1.9031
타워 delta-T | 2.5 | oC | pH | 7.8 | 7.97 | 8.8245 | [6 empty] | 7.97
증발량 | 2.4527 | m3/Hr | 표면온도 | 10 | 50 | 50 |  | 가동 스케쥴 |  |  |  | =-13.12*LOG(G9+273)+34.55 | 1.6293
비산량 | 0.13626 | m3/Hr | L.S.I | -1.0698 | 0.033587 | 2.1865 | < 2.5 | 24 | 시간/일 |  |  | =Q8-9.3-Q5-Q9+Q6+Q7 | 0.033587
보충수량 | 3.0795 | m3/Hr | 염화물 | 40 | 62 | 240 |  | 30 | 일/월
반감기 | 2.2505 | Days | 실리카 | 50 | 0 | 300 | < 150 | 12 | 월/년
Inhibitor | 초기투입 | L/Hr | L/day | L/month | L/year | Won/L | Won/year | Remarks |  |  | Iwaki
CA-31155 | 3.785 | 0.06268 | 1.5043 | 45.1293 | 541.5517 | 18800 | 10181172.7872 | 냉온수기: 1.3배 |  |  | 12.5359
CA-31855 | 5.6775 | 0.094019 | 2.2565 | 67.694 | 812.3276 | 18800 | 15271759.1808 | 냉온수기: 1.3배 |  |  | 18.8039
CA-31685 (non-P) | 1.8925 | 0.03134 | 0.75216 | 22.5647 | 270.7759 | 25200 | 6823551.9744 | 냉온수기: 1.3배 |  |  | 6.268
CA-20 | 0.94625 | 0.01567 | 0.37608 | 11.2823 | 135.3879 | 14450 | 1956355.6752 | 냉온수기: 1.3배 |  |  | 3.134
CA-34500 Silica | 1.514 | 0.025072 | 0.15043 | 3.6103 | 108.3103 | 23100 | 2501969.0573 | 냉온수기: 1.3배 |  |  | 5.0144
CA-31675 | 0.3785 | 0.006268 | 0.15043 | 4.5129 | 54.1552 | 34650 | 1876476.793 | 냉온수기: 1.3배 |  |  | 1.2536
CA-2 | 0.18925 | 0.003134 | 0.075216 | 2.2565 | 27.0776 | 147000 | 3980405.3184 | 냉온수기: 1.3배 |  |  | 0.6268
CA-1 | 0.3028 | 0.0050144 | 0.12034 | 3.6103 | 43.3241 | 55650 | 2410988.3643 | 냉온수기: 1.3배 |  |  | 1.0029
CA-9000MT | 15.14 | 0.25072 | 6.0172 | 180.5172 | 2166.207 | 15250 | 33034656.384 |  |  |  | 50.1437
CA-55N (kg) | 1.0598 | 0.01755 | 0.42121 | 12.6362 | 151.6345 | 21000 | 3184324.2547 | 용해도: 12% @25oC |  |  | 29.2505
Total Tower (1 L Pkg.) | 7.57 | 0.12536 | 3.0086 | 90.2586 | 1083.1035 | 25200 | 27294207.8976 |  |  |  | 25.0718
CA-C30 | 3.52 | 0.04562 | 1.0949 | 32.8463 | 394.1555 | 6300 | 2483179.5663 |  |  |  | 9.124
Biocide | 1회투입량 | 투입주기(일) | L/week | L/month | L/year | Won/L | Won/year | Remarks |  |  | min.
MB-215K | 2.1574 | 3.5 | 4.3149 | 18.4924 | 221.9091 | 29400 | 6524128.8 | 1/2 Hrs, pH 6.5~9.0 |  |  | 71.915 |  | CoC | 3 |  | 순환수 Silica가 150일 때 CoC 입력
MB-215 | 3.785 | 3.5 | 7.57 | 32.4429 | 389.3143 | 16200 | 6306891.4286 | 6 Hrs, pH 6.5~9.0 |  |  | 126.1667 |  | CA-31155 | 10181172.7872 | 21073426.56 | 그 때의 31155 금액을 파란셀에 "값"으로 복사
MB-1563 | 5.6775 | 3.5 | 11.355 | 48.6643 | 583.9714 | 37800 | 22074120 | 2 Hrs, pH 6.5~11.0 |  |  | 189.25 |  | Increase CoC to |  | 6 | 순환수 Silica가 250일 때 CoC 입력
MB-220 | 0.757 | 3.5 | 1.514 | 6.4886 | 77.8629 | 44650 | 3476576.5714 | 1/2 Hrs, pH 6.5~9.0 |  |  | 25.2333 |  | CA-31155 | 10181172.7872
MB-335K | 1.8925 | 14 | 0.94625 | 4.0554 | 48.6643 | 38600 | 1878441.4286 | 1~4주 당 1회 |  |  |  |  | CA-34500 | 2501969.0573
ActiChlor | 2.3845 | 3.5 | 4.7691 | 20.439 | 245.268 | 8300 | 3870367.9714 |  |  |  | 79.485 |  | Total | 12683141.8445
AquaBrom | 0.49205 | 3.5 | 0.9841 | 4.2176 | 50.6109 | 36250 |  |  |  |  | 16.4017 |  |  |  | -39.81%
ChemChlor | 3.785 | 3.5 | 7.57 | 32.4429 | 389.3143 | 23100 | 8993160 | 단위: Kg |  |  | 126.1667
CA-42171 | 1.514 | 3.5 | 3.028 | 12.9771 | 155.7257 | 30450 | 4741848 |  |  |  | 50.4667
Biocide (Continuous) | 잔류염소 | L/Hr | L/day | L/month | L/year | Won/L | Won/year | Remarks |  |  | min.
ActiChlor | 0.2 | 0.56775 | 13.626 | 408.78 | 4905.36 | 8300 | 40714488 |  |  |  | 113.55
CA-42171 | 0.2~1.5 | 0.011773 | 0.28255 | 8.4765 | 101.7175 | 30450 | 3097299.244 |  |  |  | 2.3546
Bio-dispersant | 1회투입량 | 투입주기(일) |  |  | 연소요량 | 원/L or Kg | 원/년 | Remarks
AquaSperse (1 Liter x 12) | 1.8925 | 180 |  |  | 3.785 | 29000 | 164647.5
bioeXile-L | 62.4525 | 180 |  |  | 0 | 17710 | 1106033.775
bioeXile (20 Liter) | 18.925 | 180 |  |  | 37.85 | 16800 | 953820
bioeXile (1 Liter x 12) | 18.925 | 180 |  |  | 37.85 | 27166.6667 | 1542387.5
Solid Inhibitor | 초기투입 | L/Hr | L/day | kg/month | kg/year | Won/kg | Won/year | Remarks |  |  | Iwaki
HP-55(15MT) or 25(22MT) | 3.785 | 3.134 | 75.2155 | 11.2823 | 135.3879 | 92400 | 12509845.2864 | 초기 투입: 액상 사용 |  |  | 626.796 | 5 kg/EA (Old: 100K 1.6 times)
TowerTab (kg) | 6 | 월 1회 |  | 6 | 72 | 446666.6667 | 32160000 | 200 g x 6 = 1.2 kg/pail
Solid Biocide | 1회투입량 | 투입주기(일) | kg/week | kg/month | kg/Year | Won/kg | Won/year | Remarks |  |  | min.
TowerChlor 56 (단종) | 7.57 | 3.5 | 0.3028 | 1.2977 | 15.5726 | 210132.1586 | 3272298.0491 | 대용량 펌프 |  |  | 252.3333 | 2.27 kg/EA
BioBrom C100-G | 0.04542 | 3.5 | 0.09084 | 0.38931 | 4.6718 | 173124 | 808795.7568
DuroCide C-100G | 9.084 | 3.5 | 0.09084 | 0.38931 | 4.6718 | 367500 | 1716876 | 대용량 펌프 |  |  | 302.8 | 2.27 kg/EA | =422.2/20/0.454*1200*2*1.15*6=770,000
CB-9099K | 1.514 | 7 | 1.514 | 6.4886 | 77.8629 | 33600 | 2616192 |  |  |  |  | 5 kg/pail
EnviroBrom | 1.8925 | 21 |  | 2.7036 | 32.4429 | 248292 | 8055301.8857 | pH < 9.0 |  |  |  | 100g x 25 (2.5 kg)/pail
HandiFeed |  |  |  |  | EA | Won/EA | 원
Ultra M |  |  |  |  | 1 | 450000 | 0 | HF-50@540,000 HF-100@630,000
Chill Water Loop | 구분 | 제품 | 보유수량 | 소요량 | 단위 | 단가 | Won | Remarks
| Inhibitor | CA-777 | 1 | 11.1 | Liter | 16800 | 186480 | >600 ppm NaNO2
|  | CA-999 |  | 2.4 | Liter | 16300 | 39120 | >600 ppm NaNO2
|  | CA-31685 |  | 1 | Liter | 24000 | 24000 | Shaeffler
|  | CA-58100 |  | 0.076044 | Pail | 1296000 | 98552.967 | Unit: Pail(227g x 40 = 9.1kg) |  |  |  | 3 tablet/Ton to get 600ppm NaNO2
|  | CA-53505 |  | 0.5 | Liter | 26250 | 13125 | Silicate >50 ppm SiO2 = >150 ppb PTSA
|  | CA-888 |  | 1.05 | Liter | 45150 | 47407.5 | >50 ppm Mo6 = >50 ppb PTSA
|  | CA-52525 |  | 1.5 | Liter | 63000 | 94500 | Aluminum >100 ppm Mo6 = 100 ppb PTSA
|  | CA-58200 |  | 0.23 | Kg | 324285.7143 | 74585.7143 | 91 g x 100 EA = 9.1 kg/pail
|  | Ox-Away |  | 0.1 | Kg | 18400 | 1840
|  | CA-2 |  | 0.04 | Liter | 140000 | 5600
|  | BP-10 |  |  | Liter | 8000 | 0 | To quantity is be determined by Lab Test with Actual Water
|  | BP-800 |  |  | Kg | 6500 | 0
| Biocide | MB-215 |  | 0.48 | Liter | 16200 | 7776
|  | MB-220 |  | 0.16 | Liter | 44650 | 7144 | 소요량 연4회 투입 기준
Supplemental | Initial (L) | L/Hr | L/day | L/month | L/year | Won/L | 원/년 | Remarks |  |  | Iwaki
CA-92 (Inhibitor) | 3.785 | 0.06268 | 1.5043 | 45.1293 | 541.5517 | 12850 | 6958939.9104 | 에바콘.밀폐회로냉각탑 |  |  | 12.5359
CA-92 (Descaler) | 54.0714 | 0.89542 | 21.4901 | 644.7045 | 1934.1134 | 12850 | 25548174.68 | 3개월 소요량 |  |  | 179.0846
CA-3 (Descaler) | 8.6514 | 0.14327 | 3.4384 | 103.1527 | 309.4581 | 38850 | 12358556.7168 | 3개월 소요량 |  |  | 28.6535
|  | Ox-Away |  | 13.8078
Note on C5: 타워 외부에 별도의 저수조가 있는 경우
Note on N5: = 증발량/(CoC-1)
Note on C6: Induced: 37.85 (10 gal/RT) Forced: 18.93 (5 gal/RT) Evacon: 11.36 (3 gal/RT)
Note on N6: 각 수질 측정항목의 "Cycled" 숫자가 "Limit" 숫자를 초과하지 않도록 조정
Note on C7: 1 RT = 13 liter/min (Local) US Towers: 1 RT = 3 gpm (11.355 liter/min) AWT: R = 3 gpm (11.355 lpm) x RT (Water-2000 Default)
Note on N7: = 증발량/(CoC-1)
Note on C8: 5 C: 100% 효율 2.5 C: 50% 효율 Big System: Design delta-T가 10 C인지 확인 또는 실제 (Return - Supply) 온도차 측정
Note on C9: 증발: 1oF 당 0.1% = 0.56oC 당 0.1% = 1oC 당 0.179% = 5oC 당 0.893% 이 중 80%(0.71%)가 실제 증발이고 20%는 Sensible Heat Loss On average, 80% of the cooling (=heat loss) comes from evaporation and 20% from sensible heat loss (No water loss) Colder weather reduces this factor (; the colder, the less E) delta-T 5oC일 때 순환수량의 0.72% AWT: E = 0.001 x delta-F x R x 0.8 = 0.0018 x delta-C x R x 0.8 (0.8 = Factor for Sensible Heat Loss) CA: E = 0.00085 x delta-F x RR (GPM) = 0.00153 x delta-C x RR (Ton/Hr) Jim: Calgon used 0.7 in general. Jim recommends 0.7 (30% sensible heat loss in Korea)
Note on E9: Skin Temp = 게이지 온도 + 15oC 컴프레서: 70oC
Note on C10: delta-T와 상관 없이 순환수량의 0.02% Normally ZERO (Jim on 111006) AWT: D = (0.01~0.03) x R Dependsing on the age and design of the cooling tower. Can be as low as 0.001~0.005% in new and well maintained cooling towers.
Note on C11: = 증발 + 비산 + 블로우 or E x CoC / (CoC-1) (Reference)
Note on I11: Chloride is not Limiting Factor in Water-2000
Note on C12: = 0.7 x 보유수량 / 블로우량 Time required to dilute chemical to 50% of its original concentration
Note on C15: 보유수량에 대해 100 ppm PTSA; 100 ppb
Note on D15: (블로우+비산)에 대해 100 ppm
Note on C16: 보유수량에 대해 100 ppm Moly: 0.25 ppm
Note on D16: (블로우+비산)에 대해 100 ppm
Note on C17: 보유수량에 대해 50 ppm PTSA: 50 ppb
Note on D17: (블로우+비산)에 대해 50 ppm
Note on C18: 보유수량에 대해 25 ppm
Note on D18: (블로우+비산)에 대해 25 ppm
Note on C19: 보유수량에 대해 40 ppm
Note on D19: (블로우+비산)에 대해 40 ppm
Note on C20: 보유수량에 대해 10 ppm PTSA: 40 ppb
Note on D20: (블로우+비산)에 대해 10 ppm
Note on C21: 보유수량에 대해 5 ppm Azole: 2~4 ppm
Note on D21: (블로우+비산)에 대해 5 ppm Azole: 2~4 ppm
Note on C22: 보유수량에 대해 8 ppm
Note on D22: (블로우+비산)에 대해 8 ppm
Note on C23: 보유수량에 대해 400 ppm Moly: 0.25 ppm
Note on D23: (블로우+비산)에 대해 400 ppm
Note on C24: 보유수량에 대해 28 ppm 28 x 71% converts to PO4 (20 ppm)
Note on D24: (블로우+비산)에 대해 28 ppm
Note on C25: 보유수량에 대해 100~200 ppm
Note on D25: (블로우+비산)에 대해 100~200 ppm
Note on C26: Target Ca: 10 ppm CaCl2(M.W.=111): 10 x 111/40 = 28 ppm CA-C30: 28/0.3 = 93 ppm Cl2: 93 x 0.3 x (111-40)/111 = 18 ppm 증가 Target Ca: 2 ppm CaCl2(M.W.=111): 2 x 111/40 = 5.55 ppm CA-C30: 5.55/0.3 = 18.5 ppm Cl2: 18.5 x 0.3 x (111-40)/111 = 3.55 ppm 증가 Target Ca: 5 ppm CaCl2(M.W.=111): 5 x 111/40 = 13.88 ppm CA-C30: 13.88/0.3 = 46.3 ppm Cl2: 46.3 x 0.3 x (111-40)/111 = 8.9 ppm 증가 용해도: 34g/100mL(25%) @-20℃, 37.3g/100mL(27%)@0℃ [출처] 염화칼슘(Calcium Chloride)¦작성자 주식회사 베크 Ca(HCO3)2: 보유수량에 대해 1,443 ppm Ca: 50 ppm Ca(HCO3)2: 50 x 162/40 = 202 ppm Ca(HCO3)2(14%): 202/0.14 = 1,443 ppm
Note on D26: (블로우+비산)에 대해 112 ppm
Note on C28: 57 ppm 7% vs. 20%(MB-220)
Note on C29: 100 ppm
Note on C30: 300 ppm PAG: Typical Dosage 300 ppm Maint. Dosage: 138~342 ppm Initial Dosage: 342~693 ppm Bacticide 45: 100 ppm PAG: Typical Dosage 100 ppm (90 ppm as 50%) Maint. Dosage: 53~124 ppm Initial Dosage: 124~246 ppm
Note on C31: 20 ppm PAG CheckMark 40224 Typical Dosage 10 ppm Maint. Dosage: 2.5~118 ppm Initial Dosage: 6~118 ppm CheckMark 40224 Label 25~120 ppm every 4 days or as needed
Note on C32: 50~75 ppm 산화성을 사용하고 있는 경우 15~25 ppm
Note on C33: 63 ppm 1/2 of ActiChlor alone
Note on C34: 13 ppm 1/5 amount of ActiChlor
Note on C35: Typical: 100 ppm - Min. 64 ppm [Jim-120823: Dosages can be 100 ppm two times a week, or 65 ppm 3 times a week, or 30 ppm 5 times a week.]
Note on C36: CA-Tech Bulletin HTI < 4 Hrs = 30 ppm x 7 days/week HTI 4~24 Hrs = 60 ppm x 3 days/week HTI 24~48 Hrs = 90 ppm x 2 days/week HTI > 48 Hrs = 120 ppm x 2 days/week40 ppm For Algae: 40 ppm as product (3 ppm Total Chlorine) Minimum 13.4 ppm PAG 30~90 ppm 3 to 7 times/week 1.0~1.5 ppm FRH Min. 1 hour Label Total Bromine: 1.0~9.0 ppm 2 oz/1,000 gal (15 ppm as product) = 3.4 ppm T-Br (1.47 ppm as T-Cl2) 40 ppm as product = 9.0 ppm as T-Br (÷ 2.3 = 4 ppm as T-Cl2)
Note on D38: (Target Residual Chlorine) x (Recirc.Rate; Ton/hr) x (A/100) x (100/B) = Hourly consumption (kg/hr) A: Demand or consumption ratio / 30(Winter) - 70(Summer), normally 50 with chlorine 20(Winter) - 60(Summer), normally 40 with bromine B: Chlorine content (normally 12%)
Note on D39: CONTINUOUS FEED: Apply an initial dose of 4 lb. per 10,000 gallons (48 ppm) based on system volume. Then feed at 2 lb per 10,000 gallons (24 ppm) based on system bleed and adjust feed rate to maintain 0.2 to 1.5 ppm FRH.
Note on C41: 보유수량에 대해 25~50 ppm in PAG
Note on C42: 보유수량에 대해 500x3.3=1,650 ppm
Note on C43: Maintenance & Prevention: 보유수량에 대해 500 ppm Cleaning: 보유수량에 대해 1,000 ppm
Note on C44: Maintenance & Prevention: 보유수량에 대해 500 ppm Cleaning: 보유수량에 대해 1,000 ppm
Note on C46: 보유수량에 대해 100 ppm
Note on D46: Liter/day ÷ hours/day
Note on E46: kg/month ÷ 0.005(0.5% solution) ÷ days/month
Note on F46: kg/year ÷ months
Note on G46: (블로우+비산)에 대해 25 ppm
Note on C47: 부하율 50% x 24시간/일 x 7일/주 가동하는 냉각수계에 CoC 3.0 기준 100 RT당 4개/월 투입
Note on C49: 보유수량에 대해 4 ppm (3.6~18 ppm) Matt: 2% Solution Jim's CoolCalc = 2.4 ppm APTech's PB = 2.4 ppm 0.02 lb product/1,000 gal will give 2 ppm Free Chlorine
Note on C50: 보유수량에 대해 1.2 ppm
Note on C51: APTech PB: 1.2 ppm (0.01 lb product/1,000 gal) APTech PB: 1.7% Solution 0.01 lb (product) /1,000 gal = 0.588 lb (solution)/1,000 gal Matt (211005): 0.3~0.5% Solution (0.5% in Calc-Cooling)
Note on C52: 보유수량에 대해 40 ppm US-CA Label (047C) Initial: 8 oz/10,000 gal = 6.4 ppm Maint: 0.8~1.6 oz/10,000 gal
Note on C53: EnviroTech: 1 Tablet (100g) treats 500~1,000 gallon for up to 3 weeks = 25~50 ppm PAG (EnviroBeom Tabs) Typical Dosage: 1 Tablet/1,000 gal Maint. & Initial Dosage: 1~2 tablets/1,000 gal PAG (SumpBuddy) Typical Dosage: 200 g/1.000 gal: 50 ppm Label Dosage: 200~400 g/1,000 gal: 50~100 ppm
Note on F62: APTech Product Bulletin Application/Feedrate: One L1-C Tablet per 1000 gallon doses 34.4 ppm as nitrite (as NO2). 0.5 lb/1,000 gal = 0.227 kg/3,785 L = 60 ppm increases 34.4 ppm as NO2 = 52 ppm as NaNO2 So, 600 ppm as NaNO2 = 692 ppm as Product
Note on F63: 300 ppm as product = 30 ppm as SiO2 =100 ppb as PTSA
Note on F64: 1,050 ppm as product = 50 ppm as Mo = 50 ppb as PTSA
Note on F65: 1,500 ppm as product = 100 ppm as Mo = 100 ppb as PTSA
Note on F66: Tablet (New) 48 ppm as product = 10.5 ppm Mo 230 ppm as product = 50 ppm Mo $220/9.1 kg = $24/kg x 1,200 x 1.15 x 1.15 = 38,000 Won/kg HP888STX(Cmo-C STX) 200 ppm as product = 50 ppm as Mo 0.8 lb x 30 = 24 lb(10.9 kg)/case $276/10.9 kg = $25/kg x 1,200 x 1.15 x 1.15 = 40,000 Won/kg
Note on F71: 120 ppm x 4 times a year
Note on C75: 보유수량에 대해 100 ppm
Note on D75: (블로우+비산)에 대해 100 ppm
Note on C76: 보유수량에 대해 700:1
Note on D76: (블로우+비산)에 대해 700:1
Note on C77: CA-92의 16%
Note on D77: CA-92의 16%

## Cooling-Calc-Old
Cooling Tower Water Balance and Calculation (~20220627)
입력 필요 시 조정 자동산출 고정
냉각 용량 | 1000 | RT | 항목 | 보충수 | 순환수 | Cycled | Limit | 현재 농축배수 |  | 1.55
집수조 | 0 | m3 | 전도도 | 435 | 537 | 3480 |  | 현재 블로우량 |  | 4.4771 | m3/Hr | =(LOG(G5)-1)/10 | 0.173
보유수량 | 37.85 | m3 | 총경도 | 34 | 46 | 272 |  | 목표 농축배수 |  | 8 |  | =LOG(G6)-0.4 | 1.2628
순환수량 | 684 | m3/Hr | 전알칼리 | 70 | 80 | 560 |  | 목표 블로우량 |  | 0.35177 | m3/Hr | =LOG(G7) | 1.9031
타워 delta-T | 2.5 | oC | pH | 7.8 | 7.97 | 9.0517 | [6 empty] | 7.97
증발량 | 2.4624 | m3/Hr | 표면온도 | 10 | 50 | 50 |  | 가동 스케쥴 |  |  |  | =-13.12*LOG(G9+273)+34.55 | 1.6293
비산량 | 0.1368 | m3/Hr | L.S.I | -1.0698 | 0.033587 | 2.651 | < 2.5 | 24 | 시간/일 |  |  | =Q8-9.3-Q5-Q9+Q6+Q7 | 0.033587
보충수량 | 2.951 | m3/Hr | 염화물 | 40 | 62 | 320 |  | 30 | 일/월
반감기 | 3.1383 | Days | 실리카 | 0 | 0 | 0 | < 150 | 12 | 월/년
Inhibitor | 초기투입 | L/Hr | L/day | L/month | L/year | Won/L | Won/year | Remarks |  |  | Iwaki
CA-31155 or CA-15000MT | 3.785 | 0.048857 | 1.1726 | 35.1771 | 422.1257 | 16200 | 6838436.5714 | 냉온수기: 1.3배 |  |  | 9.7714
CA-31855 or CA-8500MTP | 5.6775 | 0.073286 | 1.7589 | 52.7657 | 633.1886 | 16200 | 10257654.8571 | 냉온수기: 1.3배 |  |  | 14.6571
CA-31675 | 0.3785 | 0.0048857 | 0.11726 | 3.5177 | 42.2126 | 33000 | 1393014.8571 | 냉온수기: 1.3배 |  |  | 0.97714
CA-2 | 0.18925 | 0.0024429 | 0.058629 | 1.7589 | 21.1063 | 110000 | 2321691.4286 | 냉온수기: 1.3배 |  |  | 0.48857
CA-1 | 0.3028 | 0.0039086 | 0.093806 | 2.8142 | 33.7701 | 53000 | 1789813.0286 | 냉온수기: 1.3배 |  |  | 0.78171
CA-9000 | 15.14 | 0.19543 | 4.6903 | 140.7086 | 1688.5029 | 9700 | 16378477.7143 |  |  |  | 39.0857
CA-55N (kg) | 1.0598 | 0.01368 | 0.32832 | 9.8496 | 118.1952 | 17600 | 2080235.52 | 용해도: 12% @25oC |  |  | 22.8
Total Tower (1 L Pkg.) | 7.57 | 0.097714 | 2.3451 | 70.3543 | 844.2514 | 18000 | 15196525.7143 |  |  |  | 19.5429
CA-C30 | 7.0023 | 0.065078 | 1.5619 | 46.856 | 562.2715 | 5000 | 2811357.2571 |  |  |  | 13.0155
Biocide | 1회투입량 | 투입주기(일) | L/week | L/month | L/year | Won/L | Won/year | Remarks |  |  | min.
MB-215K | 3.785 | 3.5 | 7.57 | 32.4429 | 389.3143 | 28000 | 10900800 | 1/2 Hrs, pH 6.5~9.0 |  |  | 126.1667
MB-215 | 3.785 | 3.5 | 7.57 | 32.4429 | 389.3143 | 15400 | 5995440 | 6 Hrs, pH 6.5~9.0 |  |  | 126.1667
MB-1563 | 5.6775 | 3.5 | 11.355 | 48.6643 | 583.9714 | 36000 | 21022971.4286 | 2 Hrs, pH 6.5~11.0 |  |  | 189.25
MB-220 | 1.514 | 3.5 | 3.028 | 12.9771 | 155.7257 | 39000 | 6073302.8571 | 1/2 Hrs, pH 6.5~9.0 |  |  | 50.4667
MB-335K | 1.8925 | 14 | 0.94625 | 4.0554 | 48.6643 | 38600 | 1878441.4286 | 1~4주 당 1회
ActiChlor | 2.3845 | 3.5 | 4.7691 | 20.439 | 245.268 | 7900 | 2954895.4286 |  |  |  | 79.485
AquaBrom | 0.49205 | 3.5 | 0.9841 | 4.2176 | 50.6109 | 20100 |  |  |  |  | 16.4017
ChemChlor | 3.785 | 3.5 | 7.57 | 32.4429 | 389.3143 | 20000 | 7786285.7143 | 단위: Kg |  |  | 126.1667
CA-42171 | 1.514 | 3.5 | 3.028 | 12.9771 | 155.7257 | 23400 | 3643981.7143 |  |  |  | 50.4667
Biocide (Continuous) | 잔류염소 | L/Hr | L/day | L/month | L/year | Won/L | Won/year | Remarks |  |  | min.
ActiChlor | 0.2 | 0.57 | 13.68 | 410.4 | 4924.8 | 7900 | 38905920 |  |  |  | 114
CA-42171 | 0.2~1.5 | 0.0084425 | 0.20262 | 6.0786 | 72.9433 | 23400 | 1706873.7682 |  |  |  | 1.6885
Bio-dispersant | 1회투입량 | 투입주기(일) |  |  | 연소요량 | 원/L or Kg | 원/년 | Remarks
AquaSperse | 1.8925 | 180 |  |  | 3.785 | 27500 | 156131.25
bioeXile-L | 62.4525 | 180 |  |  | 0 | 17710 | 1106033.775
bioeXile (20 Liter) | 18.925 | 180 |  |  | 37.85 | 14300 | 811882.5
bioeXile (1 Liter x 12) | 18.925 | 180 |  |  | 37.85 | 22916.6667 | 1301093.75
Solid Inhibitor | 초기투입 | L/Hr | L/day | kg/month | kg/year | Won/kg | Won/year | Remarks |  |  | Iwaki
HP-15MT(55) or 22MT(25) | 3.785 | 2.4429 | 58.6286 | 8.7943 | 105.5314 | 66000 | 6965074.2857 | 초기 투입: 액상 사용 |  |  | 488.5714 | 5 kg/EA (Old: 100K 1.6 times)
TowerTab (kg) | 6 | 월 1회 |  | 6 | 72 | 375833.3333 | 27060000 | 200 g x 6 = 1.2 kg/pail
Solid Biocide | 1회투입량 | 투입주기(일) | kg/week | kg/month | kg/Year | Won/kg | Won/year | Remarks |  |  | min.
TowerChlor 56 | 7.57 | 3.5 | 0.3028 | 1.2977 | 15.5726 | 210132.1586 | 3272298.0491 | 대용량 펌프 |  |  | 252.3333 | 2.27 kg/EA
BioBrom C100-G | 0.04542 | 3.5 | 0.09084 | 0.38931 | 4.6718 | 173124 | 808795.7568
DuroCide C-100G | 9.084 | 3.5 | 0.09084 | 0.38931 | 4.6718 | 440528.6344 | 2058049.0875 | 대용량 펌프 |  |  | 302.8 | 2.27 kg/EA | =422.2/20/0.454*1200*2*1.15*6=770,000
CB-9099K | 1.514 | 7 | 1.514 | 6.4886 | 77.8629 | 28600 | 2226877.7143 |  |  |  |  | 5 kg/pail
EnviroBrom | 1.8925 | 21 |  | 2.7036 | 32.4429 | 248292 | 8055301.8857 | pH < 9.0 |  |  |  | 100g x 25 (2.5 kg)/pail
HandiFeed |  |  |  |  | EA | Won/EA | 원
Ultra M |  |  |  |  | 1 | 390000 | 0 | HF-50@540,000 HF-100@630,000
Chill Water Loop | 구분 | 제품 | 보유수량 | 소요량 | 단위 | 단가 | Won | Remarks
| Inhibitor | CA-777 | 6 | 66.6 | Liter | 14000 | 932400
|  | CA-999 |  | 14.4 | Liter | 12900 | 185760
|  | CA-58100 |  | 0.45626 | Pail | 1296000 | 591317.8022 | Unit: Pail(227g x 40 = 9.1kg) |  |  |  | 3 tablet/Ton to get 600ppm NaNO2
|  | CA-888 |  | 6.3158 | Liter | 39400 | 248842.1053
|  | CA-58200 |  | 1.38 | Kg | 278021.978 | 383670.3297 | 91 g x 100 EA = 9.1 kg/pail
| Biocide | MB-215 |  | 2.88 | Liter | 15400 | 44352 | 소요량 연4회 투입 기준
Supplemental | Initial (L) | L/Hr | L/day | L/month | L/year | Won/L | 원/년 | Remarks |  |  | Iwaki
CA-92 (Inhibitor) | 3.785 | 0.048857 | 1.1726 | 35.1771 | 422.1257 | 12200 | 5149933.7143 | 에바콘.밀폐회로냉각탑 |  |  | 9.7714
CA-92 (Descaler) | 54.0714 | 0.69796 | 16.751 | 502.5306 | 1507.5918 | 12200 | 19052291.8367 | 3개월 소요량 |  |  | 139.5918
CA-3 (Descaler) | 8.6514 | 0.11167 | 2.6802 | 80.4049 | 241.2147 | 34000 | 8495448.1633 | 3개월 소요량 |  |  | 22.3347
Note on C5: 타워 외부에 별도의 저수조가 있는 경우
Note on N5: = 증발량/(CoC-1)
Note on C6: Induced: 37.85 (10 gal/RT) Forced: 18.93 (5 gal/RT) Evacon: 11.36 (3 gal/RT)
Note on N6: 각 수질 측정항목의 "Cycled" 숫자가 "Limit" 숫자를 초과하지 않도록 조정
Note on C7: 1 RT = 13 liter/min (Local) US Towers: 1 RT = 3 gpm (11.355 liter/min) AWT: R = 3 gpm (11.355 lpm) x RT (Water-2000 Default)
Note on N7: = 증발량/(CoC-1)
Note on C8: 5 C: 100% 효율 2.5 C: 50% 효율 Big System: Design delta-T가 10 C인지 확인 또는 실제 (Return - Supply) 온도차 측정
Note on C9: delta-T 5 C일 때 순환수량의 0.72% AWT: E = 0.001 x (DT F) x R x 0.8 = 0.0018 x (DT C) x R x 0.8 0.8 = Factor for Sensible Heat Loss On average, 80% of the cooling (=heat loss) comes from evaporation, 20% from sensible heat loss (No water loss) Colder weather reduces this factor (; the colder, the less E) Jim(Nov.00): Calgon used 0.7 in general Jim recommends 0.7 (30% sensible heat loss in Korea)
Note on E9: Skin Temp = 게이지 온도 + 15oC 컴프레서: 70oC
Note on C10: delta-T와 상관 없이 순환수량의 0.02% Normally ZERO (Jim on 111006) AWT: D = (0.01~0.03) x R Dependsing on the age and design of the cooling tower. Can be as low as 0.001~0.005% in new and well maintained cooling towers.
Note on C11: = 증발 + 비산 + 블로우 or E x CoC / (CoC-1) (Reference)
Note on I11: Chloride is not Limiting Factor in Water-2000
Note on C12: = 0.7 x 보유수량 / 블로우량 Time required to dilute chemical to 50% of its original concentration
Note on C15: 보유수량에 대해 100 ppm PTSA; 100 ppb
Note on D15: (블로우+비산)에 대해 100 ppm
Note on H15: 210601 : 16,200-10,400-6,700-5,500
Note on C16: 보유수량에 대해 100 ppm Moly: 0.25 ppm
Note on D16: (블로우+비산)에 대해 100 ppm
Note on H16: 210601 : 16,200-9,800-7,800-6,500
Note on C17: 보유수량에 대해 10 ppm PTSA: 40 ppb
Note on D17: (블로우+비산)에 대해 10 ppm
Note on H17: 210601 : 33,000-21,400-18,700-14,500
Note on C18: 보유수량에 대해 5 ppm Azole: 2~4 ppm
Note on D18: (블로우+비산)에 대해 5 ppm Azole: 2~4 ppm
Note on H18: 160805: 110,000-77,000-54,000-46,000
Note on C19: 보유수량에 대해 8 ppm
Note on D19: (블로우+비산)에 대해 8 ppm
Note on H19: 160805: 53,000-28,800-24,000-20,000
Note on C20: 보유수량에 대해 400 ppm Moly: 0.25 ppm
Note on D20: (블로우+비산)에 대해 400 ppm
Note on H20: 210601 : 9,700-7,800-6,900-5,000
Note on C21: 보유수량에 대해 28 ppm 28 x 71% converts to PO4 (20 ppm)
Note on D21: (블로우+비산)에 대해 28 ppm
Note on H21: 210601: 17,600-14,300-11,000-9,000
Note on C22: 보유수량에 대해 100~200 ppm
Note on D22: (블로우+비산)에 대해 100~200 ppm
Note on H22: 210601 : 18,000-12,000-10,200-8,400
Note on C23: CaCl2: 92 ppm Target Ca: 20 ppm CaCl2(M.W.=111): 20 x 111/40 = 55.5 ppm CaCl2(25%): 55.5/0.3 = 185 ppm Ca(40) : Cl2(71) = Ca(20) : Cl2(17.75): 염화물 35,5 ppm 증가 물 용해도: 34g/100mL(25%) @-20℃, 37.3g/100mL(27%)@0℃ [출처] 염화칼슘(Calcium Chloride)¦작성자 주식회사 베크 Ca(HCO3)2: 보유수량에 대해 1,443 ppm Ca: 50 ppm Ca(HCO3)2: 50 x 162/40 = 202 ppm Ca(HCO3)2(14%): 202/0.14 = 1,443 ppm
Note on D23: (블로우+비산)에 대해 185 ppm
Note on H23: 210601 : 5,000-3,200-2,700-2,240
Note on C25: 100 ppm 7% vs. 20%(MB-220) PAG: Typical Dosage 100 ppm Maint. Dosage: 35~219 ppm Initial Dosage: 144~883 ppm
Note on H25: 210601 : 18,400-14,900-12,500-9,000
Note on C26: 100 ppm
Note on H26: 170901: 15,400-4,000-3,300-2,800
Note on C27: 300 ppm PAG: Typical Dosage 300 ppm Maint. Dosage: 138~342 ppm Initial Dosage: 342~693 ppm Bacticide 45: 100 ppm PAG: Typical Dosage 100 ppm (90 ppm as 50%) Maint. Dosage: 53~124 ppm Initial Dosage: 124~246 ppm
Note on H27: 190911: 20,600-11,500-9,500-8,200
Note on C28: 40 ppm PAG CheckMark 40224 Typical Dosage 10 ppm Maint. Dosage: 2.5~118 ppm Initial Dosage: 6~118 ppm CheckMark 40224 Label 25~120 ppm every 4 days or as needed
Note on H28: 210601 : 31,200-21,600-18,000-13,000
Note on C29: 50~75 ppm 산화성을 사용하고 있는 경우 15~25 ppm
Note on H29: 210601 : 38,600-26,100-20,000-16,000
Note on C30: 63 ppm 1/2 of ActiChlor alone
Note on H30: 210601 : 7,900-4,900-4,000-3,200
Note on C31: 13 ppm 1/5 amount of ActiChlor
Note on H31: 210601 : 20,100-16,800-15,600-11,000
Note on C32: Typical: 100 ppm - Min. 64 ppm [Jim-120823: Dosages can be 100 ppm two times a week, or 65 ppm 3 times a week, or 30 ppm 5 times a week.]
Note on H32: 210601 : 20,000-12,100-9,900-8,000
Note on C33: CA-Tech Bulletin HTI < 4 Hrs = 30 ppm x 7 days/week HTI 4~24 Hrs = 60 ppm x 3 days/week HTI 24~48 Hrs = 90 ppm x 2 days/week HTI > 48 Hrs = 120 ppm x 2 days/week40 ppm For Algae: 40 ppm as product (3 ppm Total Chlorine) Minimum 13.4 ppm PAG 30~90 ppm 3 to 7 times/week 1.0~1.5 ppm FRH Min. 1 hour Label Total Bromine: 1.0~9.0 ppm 2 oz/1,000 gal (15 ppm as product) = 3.4 ppm T-Br (1.47 ppm as T-Cl2) 40 ppm as product = 9.0 ppm as T-Br (÷ 2.3 = 4 ppm as T-Cl2)
Note on H33: 210601 : 23,400-16,000-13,800-11,500
Note on D35: (Target Residual Chlorine) x (Recirc.Rate; Ton/hr) x (A/100) x (100/B) = Hourly consumption (kg/hr) A: Demand or consumption ratio / 30(Winter) - 70(Summer), normally 50 with chlorine 20(Winter) - 60(Summer), normally 40 with bromine B: Chlorine content (normally 12%)
Note on H35: 210601 : 7,900-4,900-4,000-3,200
Note on D36: CONTINUOUS FEED: Apply an initial dose of 4 lb. per 10,000 gallons (48 ppm) based on system volume. Then feed at 2 lb per 10,000 gallons (24 ppm) based on system bleed and adjust feed rate to maintain 0.2 to 1.5 ppm FRH.
Note on H36: 210601 : 23,400-16,000-13,800-11,500
Note on C38: 보유수량에 대해 25~50 ppm in PAG
Note on H38: 181106: 27,500-10,000-8,500-7,000
Note on C39: 보유수량에 대해 500x3.3=1,650 ppm
Note on C40: Maintenance & Prevention: 보유수량에 대해 500 ppm Cleaning: 보유수량에 대해 1,000 ppm
Note on H40: 210601 : 14,300-8,800-6,600-5,000
Note on C41: Maintenance & Prevention: 보유수량에 대해 500 ppm Cleaning: 보유수량에 대해 1,000 ppm
Note on H41: 210601 : 275,000-187,000-143,000-110,000
Note on C43: 보유수량에 대해 100 ppm
Note on D43: Liter/day ÷ hours/day
Note on E43: kg/month ÷ 0.005(0.5% solution) ÷ days/month
Note on F43: kg/year ÷ months
Note on G43: (블로우+비산)에 대해 25 ppm
Note on H43: 210601 : 330,000-253,000-220,000-187,000
Note on C44: 부하율 50% x 24시간/일 x 7일/주 가동하는 냉각수계에 CoC 3.0 기준 100 RT당 4개/월 투입
Note on H44: 210601 : 451,000-330,000-264,000-200,000
Note on C46: 보유수량에 대해 4 ppm (3.6~18 ppm) Matt: 2% Solution Jim's CoolCalc = 2.4 ppm APTech's PB = 2.4 ppm 0.02 lb product/1,000 gal will give 2 ppm Free Chlorine
Note on C47: 보유수량에 대해 1.2 ppm
Note on C48: APTech-PB & CA-PAG: 1.2 ppm (0.01 lb product/1,000 gal) APTech-PB: 1.7% Solution 0.01 lb (product) /1,000 gal = 0.588 lb (solution)/1,000 gal Matt (211005): 0.3~0.5% Solution (0.5% in Calc-Cooling)
Note on H48: 211213 (kg): 440,529-308,370-264,317-220,264 (2.27kg Bottle): 1,000,000-700,000-600,000-500,000
Note on C49: 보유수량에 대해 40 ppm US-CA Label (047C) Initial: 8 oz/10,000 gal = 6.4 ppm Maint: 0.8~1.6 oz/10,000 gal
Note on H49: 210601 : 143,000-88,000-73,700-63,800
Note on C50: EnviroTech: 1 Tablet (100g) treats 500~1,000 gallon for up to 3 weeks = 25~50 ppm PAG (EnviroBeom Tabs) Typical Dosage: 1 Tablet/1,000 gal Maint. & Initial Dosage: 1~2 tablets/1,000 gal PAG (SumpBuddy) Typical Dosage: 200 g/1.000 gal: 50 ppm Label Dosage: 200~400 g/1,000 gal: 50~100 ppm
Note on H56: 210601: 14,000-9,500-8,500-7,500
Note on H57: 210601: 12,900-9,000-7,500-6,500
Note on F58: APTech Product Bulletin Application/Feedrate: One L1-C Tablet per 1000 gallon doses 34.4 ppm as nitrite (as NO2). 0.5 lb/1,000 gal = 0.227 kg/3,785 L = 60 ppm increases 34.4 ppm as NO2 = 52 ppm as NaNO2 So, 600 ppm as NaNO2 = 692 ppm as Product
Note on H58: 210601 : 1,296,000-929,000-799,200-691,200
Note on F59: 1,050 ppm as product = 50 ppm as Mo
Note on H59: 210601: 39,400-19,000-16,000-14,000
Note on F60: Tablet (New) 48 ppm as product = 10.5 ppm Mo 230 ppm as product = 50 ppm Mo $220/9.1 kg = $24/kg x 1,200 x 1.15 x 1.15 = 38,000 Won/kg HP888STX(Cmo-C STX) 200 ppm as product = 50 ppm as Mo 0.8 lb x 30 = 24 lb(10.9 kg)/case $276/10.9 kg = $25/kg x 1,200 x 1.15 x 1.15 = 40,000 Won/kg
Note on H60: 210601 : 2,530,000-1,870,000-1,540,000-1,200,000
Note on F61: 120 ppm x 4 times a year
Note on H61: 170901: 15,400-4,000-3,300-2,800
Note on C64: 보유수량에 대해 100 ppm
Note on D64: (블로우+비산)에 대해 100 ppm
Note on H64: 171123: 12,200-6,000-5,000-4,000
Note on C65: 보유수량에 대해 700:1
Note on D65: (블로우+비산)에 대해 700:1
Note on H65: 171123: 12,200-6,000-5,000-4,000
Note on C66: CA-92의 16%
Note on D66: CA-92의 16%
Note on H66: 111130: 34,000-22,000-*-*

## TowerTabCalc
TowerTab 및 CB-9099 연간 소요량 산출 (예: 50~100% Load x 24시간/일 x 7일/주 x 12개월/년)
CoC=6 | 25 RT |  | 50 RT |  | 100 RT |  | 150 RT |  | 200 RT |  | Unit Price
| Pail | Amount | Pail | Amount | Pail | Amount | Pail | Amount | Pail | Amount
TowerTab | 0.375 | 307500 | 0.75 | 615000 | 1.5 | 1230000 | 2.25 | 1845000 | 3 | 2460000 | 820000
| 0.5 | 개/월 | 1 | 개/월 | 2 | 개/월 | 3 | 개/월 | 4 | 개/월
CB-9099 | 0.5 | 41000 | 1 | 82000 | 2 | 164000 | 3 | 246000 | 4 | 328000 | 82000
| 0.5 | 개/2주 | 1 | 개/2주 | 2 | 개/2주 | 3 | 개/2주 | 4 | 개/2주
Weekly Timer | 1 | 55000 | 1 | 55000 | 1 | 55000 | 1 | 55000 | 1 | 55000 | 55000
Solenoid Valve | 1 | 48000 | 1 | 48000 | 1 | 48000 | 1 | 48000 | 1 | 48000 | 48000
Total | 451500 |  | 800000 |  | 1497000 |  | 2194000 |  | 2891000
CoC=3 | 25 RT |  | 50 RT |  | 100 RT |  | 150 RT |  | 200 RT |  | Unit Price
| Pail | Amount | Pail | Amount | Pail | Amount | Pail | Amount | Pail | Amount
TowerTab | 0.75 | 615000 | 1.5 | 1230000 | 3 | 2460000 | 4.5 | 3690000 | 6 | 4920000 | 820000
| 1 | 개/월 | 2 | 개/월 | 4 | 개/월 | 6 | 개/월 | 8 | 개/월
CB-9099 | 0.5 | 41000 | 1 | 82000 | 2 | 164000 | 3 | 246000 | 4 | 328000 | 82000
| 0.5 | 개/2주 | 1 | 개/2주 | 2 | 개/2주 | 3 | 개/2주 | 4 | 개/2주
Weekly Timer | 1 | 55000 | 1 | 55000 | 1 | 55000 | 1 | 55000 | 1 | 55000 | 55000
Solenoid Valve | 1 | 48000 | 1 | 48000 | 1 | 48000 | 1 | 48000 | 1 | 48000 | 48000
Total | 759000 |  | 1415000 |  | 2727000 |  | 4039000 |  | 5351000
TowerTab is to be sold by Pail base at the unit price in the far right column. For small systems, 1/2 Pail can be sold.
TowerTab: 기본 판매 단위는 페일이며, 1/2 페일 단위로 판매할 수도 있음. 표 맨 우측의 단가를 참조할 것.
1 Pail = 2.7 kgs = 16 Tablets @820,000 Won 1/2 Pail = 1.35 kgs = 8 Tablets @410,000 Won
CB-9099 is to be sold by Pail pase at the unit price in the far roght column. It is not to be sold by 1/2 Pail.
CB-9099: 기본 판매 단위는 페일이며, 1/2 페일로 판매할 수 없음. 표 맨 우측의 단가를 참조할 것.
1 Pail = 5 kgs = 25 Tablets @82,000 Won
Timed Blow System을 포함해도 Liquid Program 가격의 90% 수준